## Sheet1
Heat Balance Calculation Sheet - Part B
AB&CO Process Heating
For balancing temperatures, flows and capacities of the steam heating of liquid or gas.
Medium - Cold Side
Temperature, Inlet | 20 | °C = | 68 | °F
Temperature, Outlet | 50 | °C = | 122 | °F
Specific Heat | 4.1868 | kJ/(kg°C) = | 0.99995 | BTU/(lb°F)
Mass Flow | 10000 | kg/h = | 22050 | lb/h
Medium - Steam Side
Pressure (above atm.) | 6 | bar g | 87.0221 | psig
Temperature, Inlet | 165 | °C = | 329 | °F
Temperature, Outlet | 165 | °C = | 329 | °F
Evaporation Heat | 2064.94 | kJ/kg = | 887.7226 | BTU/lb
Steam Consumption | 608.2695 | kg/h = | 1341.2342 | lb/h
Capacity: | 348.9 | kW = | 1189749 | BTU/h
AB&CO - TT BOILERS A/S ¦ Copenhagen, Denmark ¦ T: +45 4817 7599 W: www.abco.dk
Database for vanddamp i tørmættet tilstand
[5 empty] | DAMPTRYK (BARA) | TEMP. (°C) | HEAT OF EVAPORATION
(kJ/kgK)
[5 empty] | 0.1 | 45.8 | 2392.97
[5 empty] | 0.15 | 53.997 | 2373.2
[5 empty] | 0.173 | 57 | 2366
[5 empty] | 0.2 | 60.1 | 2358.45
[5 empty] | 0.25 | 64.992 | 2346.4
[5 empty] | 0.3 | 69.5 | 2334
[5 empty] | 0.35 | 72.5 | 2323.5
[5 empty] | 0.375 | 74.193 | 2321.25
[5 empty] | 0.4 | 75.886 | 2319
[5 empty] | 0.45 | 78.693 | 2311.5
[5 empty] | 0.5 | 81.5 | 2304
[5 empty] | 0.65 | 87.5 | 2289
[5 empty] | 0.8 | 93.5 | 2274
[5 empty] | 1 | 99.63 | 2257.89
[5 empty] | 1.06 | 101.3 | 2254.3
[5 empty] | 1.1 | 102.32 | 2250.76
[5 empty] | 1.3 | 106.81 | 2238.555
[5 empty] | 1.5 | 111.3 | 2226.35
[5 empty] | 1.75 | 115.75 | 2213.975
[5 empty] | 2 | 120.2 | 2201.6
[5 empty] | 2.25 | 123.8 | 2191.35
[5 empty] | 2.5 | 127.4 | 2181.1
[5 empty] | 2.75 | 130.45 | 2172.185
[5 empty] | 3 | 133.5 | 2163.27
[5 empty] | 3.5 | 138.9 | 2147.37
[5 empty] | 4 | 143.6 | 2132.93
[5 empty] | 4.5 | 147.9 | 2119.76
[5 empty] | 5 | 151.8 | 2107.38
[5 empty] | 5.5 | 155.5 | 2095.9
[5 empty] | 6 | 158.8 | 2085.08
[5 empty] | 6.2 | 160 | 2081.3
[5 empty] | 6.5 | 162 | 2074.77
[5 empty] | 6.7 | 163 | 2071.4
[5 empty] | 7 | 165 | 2064.94
[5 empty] | 7.5 | 167.8 | 2055.5
[5 empty] | 8 | 170.4 | 2046.56
[5 empty] | 8.5 | 172.9 | 2037.87
[5 empty] | 9 | 175.4 | 2029.46
[5 empty] | 9.5 | 177.7 | 2021.38
[5 empty] | 10 | 179.9 | 2013.59
[5 empty] | 10.5 | 182 | 2006.4
[5 empty] | 11 | 184.1 | 1998.58
[5 empty] | 11.5 | 186 | 1991.3
[5 empty] | 11.7 | 187 | 1988.48
[5 empty] | 12 | 188 | 1984.27
[5 empty] | 12.2 | 188.7 | 1981.57
[5 empty] | 13 | 191.6 | 1970.7
[5 empty] | 13.5 | 193.3 | 1964.1
[5 empty] | 14 | 195 | 1957.73
[5 empty] | 14.5 | 196.8 | 1951.6
[5 empty] | 15 | 198.3 | 1945.24
[5 empty] | 15.5 | 199.85 | 1939.2
[5 empty] | 16 | 201.4 | 1933.14
[5 empty] | 16.5 | 202.86 | 1927.3
[5 empty] | 17 | 204.3 | 1921.56
[5 empty] | 17.5 | 205.72 | 1915.9
[5 empty] | 18 | 207.1 | 1910.23
[5 empty] | 18.5 | 208.47 | 1904.7
[5 empty] | 19 | 209.8 | 1899.29
[5 empty] | 19.5 | 211.1 | 1893
[5 empty] | 20 | 212.4 | 1888.61
[5 empty] | 21 | 214.8 | 1878.38
[5 empty] | 22 | 217.2 | 1868.15
[5 empty] | 23 | 219.5 | 1858.31
[5 empty] | 24 | 221.8 | 1848.47
[5 empty] | 25 | 223.9 | 1839.075
[5 empty] | 26 | 226 | 1829.68
[5 empty] | 26.5 | 227 | 1825.1
[5 empty] | 27 | 228 | 1820.6
[5 empty] | 27.5 | 229 | 1815.8
[5 empty] | 28 | 230 | 1811.52
[5 empty] | 29 | 231.9 | 1802.71
[5 empty] | 30 | 233.8 | 1793.9
[5 empty] | 31 | 235.7 | 1785.4
[5 empty] | 33 | 239.18 | 1768.6
[5 empty] | 35 | 242.5 | 1752.2
[5 empty] | 37 | 245 | 1736.2
[5 empty] | 40 | 250 | 1712.9
[5 empty] | 42 | 253 | 1697.8
[5 empty] | 45 | 257 | 1675.6
[5 empty] | 47 | 260 | 1661.1
[5 empty] | 50 | 264 | 1639.7
[5 empty] | 55 | NA | NA
[5 empty] | 56.5 | NA | NA
[5 empty] | 57 | NA | NA
[5 empty] | 58 | NA | NA
[5 empty] | 59 | NA | NA
[5 empty] | 60 | NA | NA
[5 empty] | 63.3 | NA | NA
[5 empty] | 90 | NA | NA